UNAVCO Polar Remote Site Visit Checklist		Version 1.0, December 21 2012	PAGE 1 OF 2

Station ID	____________	Date  UTC  _______________   Time UTC  _______________

Personnel	________________________________________________________________

INSPECTION ON ARRIVAL						PHOTOS ON ARRIVAL

□ GPS antenna secure on mast?					□ General site photo

□ GPS antenna mast stable?						□ GPS antenna, mast, and cable

□ GPS antenna cable damaged?					□ Frame, front side

□ Solar panels or cables damaged?					□ Frame, back side

□ Wind turbines or cables damaged?					□ Connectors on outside of enclosure

□ Weather station or cable damaged?					□ Close up of anything broken

□ Iridium antenna(s) or cable(s) damaged?				□ Inside the main enclosure

□ Frame stable with joints intact?					□ Connectors on inside of enclosure

□ Connectors secure on outside of enclosure?				□ GPS electronics board

NETRS FRONT PANEL		   NETR9 FRONT PANEL		SOLAR AND WIND REGULATOR LED’S

□ Satellite:   	red 1Hz		   □ Lower Left:    Logging / USB	□ Solar charge: green, or red with green flash

□ Data:       	yellow 1Hz	   □ Upper Left:	    SV X    (X>5)		□ Solar LVD: 	 green

□ Power A:  	solid green	   □ Upper Right:  Battery icon		□ Wind charge: green, or red with green flash

□ Power B: 	solid yellow

KNOWN MAINTENANCE TASKS  (SITE SPECIFIC – MAKE LIST PRIOR TO SITE VISIT)

□ _______________________________________	□ ___________________________________________

□ _______________________________________	□ ___________________________________________

□ _______________________________________	□ ___________________________________________

□ _______________________________________	□ ___________________________________________

□ _______________________________________	□ ___________________________________________

NOTES

UNAVCO Polar Remote Site Visit Checklist		Version 1.0, December 21 2012	PAGE 2 OF 2

Station ID	____________	Date  UTC  _______________   Time UTC  _______________

CHECKLIST BEFORE DEPARTURE

GPS receiver UID	____________			GPS receiver firmware			____________

Primary Iridium UID	____________			Primary timer switch on/off settings	____________

Secondary Iridium UID	____________ 			Secondary timer switch on/off settings	____________

Weather station UID	____________ 			Met height above/below (+/-) GPS ant. 	____________

CHECK VOLTAGES	(see MEASURING VOLTAGES section in Remote Site Visit Procedures)

Breakers OFF	Main battery_________	Aux bank 1  _________	    Aux bank 2  _________    Aux bank 3  _________

Solar 1 	       _________	Solar 2         _________	    Solar 3         _________    Solar 4         _________

Wind 1	       _________	Wind 2         _________

Heat pad Ω _________

Breakers ON	Load V	       _________

□ All connectors attached to INTERNAL enclosure wall

□ All connectors attached to EXTERNAL enclosure wall

NETRS FRONT PANEL		   NETR9 FRONT PANEL		SOLAR AND WIND REGULATOR LED’S

□ Satellite:   	red 1Hz		   □ Lower Left:    Logging / USB	□ Solar charge: green, or red w/green flash

□ Data:       	yellow 1Hz	   □ Upper Left:	    SV X    (X>5)		□ Solar LVD: 	 green (magnet to reset if red)

□ Power A:  	solid green	   □ Upper Right:  Battery icon		□ Wind charge: green, or red w/green flash

□ Power B: 	solid yellow

□ Secondary Iridium check, if installed (use active SIM)

□ Move active SIM to primary modem, backup SIM to secondary

□ Interior Photographs		□ Close-ups of GPS electronics board	□ Overall view inside the main enclosure

□ Power connectors on enclosure wall	□ RF and ground cables on enclosure wall

□ Anti-static bag, alligator clip leads, ground wires

□ Verify all breakers on (red showing)

□ Enclosures closed, latched, and strapped

□ Exterior Photographs	□ Frame, front side	□ Frame, back side	□ Connectors on enclosure wall

□ Top rail: Met, Iridium □ Anything damaged	□ Anything you changed

□ Primary Iridium check

NOTES